## Sheet1
WMATA WORK LIST
Item Number | Description | Area/ Segment or Building | Specific Location | Technical Requirements | Discipline | Originator | Remarks | Photos
N99 GHB fibber patchcords needs rerouting so cabinet can be pulled out to access rear for service. | N99 | WHB | 27-02-30 FOS | Systems | D. Ansara |  | N99 GHB cabinet fiber needs rerouting | N99 WHB Comm Rm Patch cords need to be rerouted
N99 WHB Patch cords not routed correctly. | N99 | WHB | 27_20_00 LAN & 27-02-30 FOS | Systems | D. Ansara |  | N99 WHB Comm Rm Patch cords need to be rerouted | N99 WHB Comm Rm Copper cable needs label
N99 WHB Cat6 cable needs label. | N99 | WHB | 27_20_00 LAN | Systems | D. Ansara |  | N99 WHB Comm Rm Copper cable needs label | N99 WHB Comm Rm Conduits not labeled or firestopped
N99 GHB Communication room conduits are not labeled of firestopped. | N99 | WHB | 27_05_10 Equip & Material | Systems | D. Ansara |  | N99 WHB Comm Rm Conduits not labeled or firestopped | N99 WHB Comm Rm rack needs power strips.
N99 WHB rack requires vertrical power strips to be installed on rear rails for installed equipment to connect to. | N99 | WHB | 27_20_00 LAN | Systems | D. Ansara |  | N99 WHB Comm Rm rack needs power strips. | N99 WHB Comm Rm Switch only with one Power supply
N99 WHB Comm room switch not equiopped with second power supply. | N99 | WHB | 27_20_00 LAN | Systems | D. Ansara |  | N99 WHB Comm Rm Switch only with one Power supply | N99 WHB Comm Rm active equip not grounded
N99 WHB Comm Rm active equipment not grounded. | N99 | WHB | 27_20_00 LAN | Systems | D. Ansara |  | N99 WHB Comm Rm active equip not grounded | N99 WHB Comm Rm UPS whips laying on floor.
N99 WHB Comm Rm. UPS whips not secured and lying on floor. | N99 | WHB | 27_20_00 LAN | Systems | D. Ansara |  | N99 WHB Comm Rm UPS whips laying on floor.