## List
WMATA SCI IDENTIFIED ITEMS
Item Number | Description | Area/ Segment or Building | Specific Location | Technical Requirements | Discipline | Originator | Remarks | Photos
1 | Sliding Gate w/ Service Counters - Weight of pull-up sliding panels are difficult to lift while standing behind shelf and means are not provided to secure in raised position. This condition presents a potential safety issue if the panel is accidently dropped on a hand/arm. | WHB | 101 | N00-WHB-A-112/202, PB02253, Design Change 0880: Drop Down Counter | Architecture | S. Peterson | A design for these sliding panels was not developed and submitted for review and approval in the design drawings and shop drawings. Replacement panel(s) should be designed to eliminate safety issue and provide convenience for user. | WHB-Video 1.mov
2 | Sliding Gate w/ Service Counters - A caster was added to the rolling gate with the sliding service panels which can become stuck when pushing open. | WHB | 101 | N00-WHB-A-112/202, PB02253, Design Change 0880: Drop Down Counter | Architecture | S. Peterson | The incorporation of this caster was not submitted for approval. Other means to support the weight of gate should be considered including using lighter material for the sliding service panels. | WHB-SP-1.jpg
3 | Service Counter panel on south end does not have means to secure with a padlock. | WHB | 101 | N00-WHB-A-112/202, PB02253, Design Change 0880: Drop Down Counter | Architecture | S. Peterson | A design for these sliding panels was not developed and submitted for review and approval in the design drawings and shop drawings. All panels should have ability to secure with lock. | WHB-SP-2.jpg
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
354
355
356
357
358
359
360
361
362
363
364
365
366
367
368
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
503
504
505
506
507
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
701
702
703
704
705
706
707
708
709
710
711
712
713
714
715
716
717
718
719
720
721
722
723
724
725
726
727
728
729
730
731
732
733
734
735
736
737
738
739
740
741
742
743
744
745
746
747
748
749
750
751
752
753
754
755
756
757
758
759
760
761
762
763
764
765
766
767
768
769
770
771
772
773
774
775
776
777
778
779
780
781
782
783
784
785
786
787
788
789
790
791
792
793
794
795
796
797
798
799
800
801
802
803
804
805
806
807
808
809
810
811
812
813
814
815
816
817
818
819
820
821
822
823
824
825
826
827
828
829
830
831
832
833
834
835
836
837
838
839
840
841
842
843
844
845
846
847
848
849
850
851
852
853
854
855
856
857
858
859
860
861
862
863
864
865
866
867
868
869
870
871
872
873
874
875
876
877
878
879
880
881
882
883
884
885
886
887
888
889
890
891
892
893
894
895
896
897
898
899
900
901
902
903
904
905
906
907
908
909
910
911
912
913
914
915
916
917
918
919
920
921
922
923
924
925
926
927
928
929
930
931
932
933
934
935
936
937
938
939
940
941
942
943
944
945
946
947
948
949
950
951
952
953
954
955
956
957
958
959
960
961
962
963
964
965
966
967
968
969
970
971
972
973
974
975
976
977
978
979
980
981
982
983
984
985
986
987
988
989
990
991
992
993
994
995
996
997
998
999
1000

## Sheet3 (hidden)
Specific locations
Segments |  | 117
N00 | Disciplines | 119
N06 | ATC | 2905
N07 | Civil | IB Track sta. 1340+29.58
N07 and N08 | Closeout | #10 DXO 14.00' switch machines
N07, N08, N09, and N96 | COMM | 001 Elevator Machine Rm
N08 | Electrical | 001 Elevator Machine Rm 108 EMR Vestibule
N08 Interlocking | ELES | 100 All Elevators
N08, N10, N11 & N12 | Facilities | 100 All Escalators
N08. N97, N98A, N99E, N11, N12 | Mech | 100 ECR
N09 | PWR | 100 ECR & 101 ECR
N10 | Quality | 100 ECR & 102 ECR
N10, N97 & N98A | SCADA | 100 ECR, 101 ECR
N11 | Structure | 100 ECR, 109 Elec Cab Rm
N11 & N12 | Systems | 100 ECRs
N11, N12, and N98B | Track | 100 Elevators at Station
N12 |  | 100 Water Serv Rm
N96 |  | 100 Water Service Room
N97 |  | 101 Cart Storage Rm, south entrance
N98 |  | 101 ECR
N98A |  | 101 ECR 103 EMR
N98B |  | 101 Water Serv Rm
N99E |  | 102 Cleaners Rm
102 Cleaners Rm 102
102 Cleaners Room -102
102 ECR
102 EMR
102 EMR-102
102 Sprinkler Rm
103 Cart Rm
103 Cart Rm 103
103 ECR
103 ECR and 225 AC Swchbd Rm
103 EMR
103 Platform, south of the Elevator Machine Room 103, CL 12.2
104 Elevator Machine Rm
104 Elevator Machine Rm and 102 escalator control rm
104 Fire Equip Cab
104 Maint Rm
104 Maint Rm, and Public washrooms 205 & 207
104 Sewage Ejector Rm
104 Sewage Ejector Rm, 106 Pump Rm
104 Water Serv Rm
105 Cleaner Rm
105 Cleaner Rm and 103 Elec Cab Rm
105 Elect Cab Rm
105 Elect Cabinet Rm
105 Elect Cabinet Rm & Cart Rm 103
105 EMR
105 Platform, north of the Water Service Room 105, CL 19.3
105 Water Serv Rm
105 Water Serv Rm, and 117 TCR
105 Women's Public Washroom
106 Elect Cab Rm
106 Elect Cab Rm 106
106 Maint Rm
106 Maintenace Room - 106
106 Platform, between CL 01 & 1, IB side, next to Water Service Room 106
106 Pump Rm
106 Service corridor, north of Water Service Room 106
106 TeleCOMM Rm
106 Water Serv Rm
106 Water Serv Rm & Elect Cabinet Rm 108
106 Water Service Rm
106 Water Service Rm- closed
107 Fire Equipment Rm
107 Train Supervisors Rm
108 CER
108 Cleaner's Rm
108 Elect Cabinet Rm
108 Fire Equip Cab
1080+31, N1 and N2
109 Cleaner's Rm
109 Cleaner's Rm & Maint Rm 111
109 Cleaners Rm
109 Elect Cab Rm
109 Maintenance Rm
109 Men's Public Washroom
110 COMM Rm
110 Elect Cab Rm
110 Platform Train control room 110
110 TCR
110 Telecomm Rm
110 Telecomm Rm 110
111 CER Rm
111 Comm Rm
111 Maint Rm
111 Maint. Rm
111 Train Op. Dispatchers Rm
112 Elect Cab Rm
112 Exhaust Vault
112 Telecomm Rm 112
1120 Mezzanine (Paid)
113 CER
113 CER 113
113 Comm Rm
113 Men's Employee Washroom
113 TCR
113 Train Op. Lockers Rm
114 Corridor
114 Electr Cable Rm
114 Emerg Egress Stair
1140+10 to 1141+28
1140+61 to 1141+20
115 Emerg Egr Stair
115 TCR
115 Train Op. Lockers Rm
116 Emerg Egr Stair
116 Maint Rm
117 Lunch Rm
117 TCR
117 TCR, North Wall stub-ups, 1202+49
117 Train Op. Washroom
1170 Mezzanine (Unpaid)
119 CER
119 CER / Upper South wall
119 CER Rm, S103 Elec Cab Rm
119 Escalator Machine Rm
120 Mech Rm
122 Emergency Stair 4
124 W Elect Cab Rm
125 Elect Cab Rm
126 Telephone Rm
1262 + 90 IB
127 Elect Cable Rm
129 East emerg egress stair
1462+00
1526+70 to 1530+30
153+64.12
1533+69.78
200 All Public washrooms
200 All Public washrooms
200 Public wash rooms
200 Public washrooms
200 Washrooms
200 Washrooms and Lunch Room
201 Public Washroom
2010 Mezz Paid Area
2010 Mezz Paid Area, Kiosk
202 Corridor 210 Mech Space
202 Public Washroom
202 Public Washroom 208
2020 Mezzanine (Paid)
203 Public Washroom
203 Yard Storage Room
204 Emergency Stair 4
204 Public Washroom
204 Public Washroom 204
2040 Kiosk
205 Public washroom
206 Public Washroom
206 Public washroom 206
206 TCR
208 Cleaner's Rm
208 Door #208 Entrance to corridor
208 Public washroom
208 Service Corridor
208 Service Corridor, between CL 01 and CL 1, next to the electric water coolers.
208 Service corridor, north of Telecomm Room 1 (TE1) 110 – CL01
209 Service Corridor
209 Service Corridor, between CL 16 and CL 17, next to the electric water coolers.
2090 Mezz Unpaid Area
210 Kiosk
210 Mech Space
210 Women's Washroom
211 Fire Equip Rm
211 Police Rm
212 Mech Rm
212 Men's and 210 Women's Washrooms
212 Men's Washroom
212 Men's Washroom
212 Men’s washroom
212 Service corridor
213 Elect Cab Rm
214 CER
214 Cleaner's Rm
214 Cleaners Rm
214 Women washroom
215 Cleaners Rm
215 Cleaners Rm CP-1 and over lamp
216 Emergency Stair 8 & 9
216 Mech Room
216 Mechanical Rm
216 Men washroom 216
216 Men's washroom
217 Elect Cab Rm
217 Lunch Rm
218 AC Swbrd Rm
218 AC Swbrd Rm & 220 Battery Rm
218 AC Switchboard Rm
218 Battery Rm
218 Cleaners Rm
219 Telecomm Rm
220 Battery Rm
220 Elect Cab Rm
220 Mech Rm
220 Mezzanine mechanical room 220
220 Rm
221 Battery Rm
221 Battery Rm 223 AC Swgr
221 Battery Rm, 105 Water Serv Rm and 109 Elect Cab Rm
221 Comm EF Rm
222 AC Mech Rm
222 AC Switchboard Rm 222
222 AC Swtchbrd Rm
222 Elect Cabinet Rm
222 Lunch Rm
223 AC Switchboard Rm
223 Battery Rm
2230 Exit corridor
224 Battery Rm
224 Battery Rm 224
224 Loading Dock
224 Lunch Rm
225 AC Swchbd Rm
225 Mech Rm
226 COMM EF
226 Elect Cab Rm
226 Elect Cab Rm 226
226 TPSS 16
227 Cleaner's Rm
227 Mech Rm
227 Mechanical Room 227 – at the SE corner CL19.3
228 AC Swbd Rm
228 Lunch Rm
228 Lunch Rm 228
228 Transformer Courtyard
229 Women's Washroom
229 Women’s Washroom
230 COMM EF 230
231 Men's Washroom
233 Lunch Rm
3000 Platform
3000 Platform. West Serv Aisle OB, behind blue light station.
3000 Station Platform
303 Cart Storage Rm
305 Area of Rescue Assistance
306 Elect Cab Rm
307 Telecomm Rm 1
308 Telecomm Rm 2
310 Area of Rescue Assistance
312 Cleaner's Rm
34.5 KV MHs 12, 15, 16, 17 , 18 & 20, west of 607 overpass.
34.5MHW.21
34.5MHW.22
34.5MHW.23
3BT track circuit
606 & 772 Sation Tub Area
606 Sation and NP.MH.01
606.NP.MH.01
Abutment A wall
AC Switchgear Room
aerial guideway
Aerial Piers
ALL AC Switchgear Rooms
All around Innovation Station- closed
All Birdwire Locations
All Station stairs
ALL Station Unit substation rooms
All stations
ALL TBSs
ALL TCR
All TCRs visited so far
All TPSS
All TPSS Manholes
ALL TPSS transformers
ALL TPSS, TBS, AC rooms
All Wayside TPSS
Around CL-9 OB side
Ashburn Station
At several supports, north and south sides
ATC Signals Interlockings at ballasted track
Ballasted area, west of 112 Elect Cab Rm CL-01.6, Axis F
barrier wall
Barrier wall CL12 OB, street side
barrier wall- closed
Below Elevator Machine Room
Below Platform CL 0.2, IB side
Below Platform CL 13.5, IB side
Below platform, between CL 01 & 1, OB side
Between HPB & Abut A, Both Sides
Bridge IB Side- closed
Cerntreville Road Bridge
cinder bricks
CL 20.6 IB Side
Cleaners Rm 218
CM 1377+00 OB side; East of Innovation Station, IB side
CM# N1&N2 1338+50.
concrete
Concrete cracks
control joint
East and West Safe Dispersal Areas
East and West Service Aisles
East Safe Dispersal Area
East Safe Dispersal Area IB side
East Safe Dispersal Area, OB side
East Serv Area Street level
East Serv Rm wall, outside face, OB side
East Service Aisle
East Service Rooms
East: 1)PA-P-036=OB and 1)PA-P-035=IB West 1) PA-P-006=OB 2) PA-P-005=IB
ECR N101
Elev 1 and 4
Elevator 4
Elevator 6
Elevator 6 back frame
Elevator 6 hoistway
Elevator Machine Room and escalator control room
Elevator Machine Rooms
Elevator pit
Elevators
Elevators
Elevators 1 & 2
Elevators 3 & 4
Elevators 5 & 6
ELT- closed
Emerg Egress Stair
EMR; Platform level
End of Platforms, both ends
Escalator 3
Escalator 4 (whole chain)
Escalator 5
Escalator 5 (whole chain)
Escalator 6
Escalator Control Room
Escalators
Escalators
Escalators 1 & 2
Escalators 1, 2, 3
Escalators 3 & 4
Escalators 5 & 6
ETS telephone terminations
Fence Along Track
Footings- closed
From Sta. 1145+00 to 1205+00
From vista switches to Station; both feeders
Girder 60A
Girder 60D
girder 72B
Girders
Guideway
Guideway cm 1293+83 OB
Guideway IB side sta. 1340+29.56
Guideway Platform Level
Guideway, west end of platform
Herndon IB & OB East
Herndon Station track level, OB side
hollowcore planks
Horsepen Run Bridge
IB & OB tracks cm 1379+50 to 1516+00
IB Trackwall at cm 1185+11
IB Trackwall, cm 1198+28
IDW subzone boxes
Ijs and crossbonds
In front and inside of Emerg. Egrs. Stair, & Safe Dispersal Areas
InBound Track, Facing Point Left Hand Turnout. Sta. 1294 + 00
Innovation Station, Emergency Egress Stail 118, West Side… As well as all other stations respectively
Interlocking
Interlockings
Kiosk
Kiosks
Land Bridge, both sides and all parapet walls
masonry wall
Mezz Level
Mezz Level and South Pavilion
Mezz level around Esc and stairs
Mezz Level at Ped Bridges juncture
Mezz level in front of TVM
Mezz Level Kiosk
Mezz level service rooms
Mezz Level, around CCTV camera over TVM
Mezz Level, at escalator exit
Mezz Level, behind map case
Mezz Level, Center aisle between washrooms
Mezz Level, CL-1 to North Ped Bridge
Mezz level, escalator 5 RTC-275
Mezz Level, Fare Collection area
Mezz Level, next to stair 4; RTC-154
Mezz Level, Outside lower unit
Mezz Level, over TVM
Mezz level, Paid Area
Mezz level, Public washroom façade
Mezz level, Unpaid Area
Mezzanine Level- closed
ML Abut B, Ret. Wall, OB Side
N00- closed
N00/ All Interlocking Locations
N07-N08-N09-N96
N08 Interlocking N2 1195+76
N09
N09 Track Side between CL 1&2
N1 & N2-1202+88
N1 & N2-1203+00
N1-1132+85
N1-1133+04
N1-1142+71
N1-1146+43
N1-1176+82
N1-1196+50
N1-1211+28 to N1-1212+35
N1-1211+71
N1-1211+85
N1-1217+00
N1-1217+78
N1-1220+88
N1-1243+56
N1-1253+34
N1-1526+59
N1-1545+51
N1-1564+52
N1-1565+65 IB
N1-1567+45
N1-1567+50
N1-1569+04
N1-1569+06
N1-1573+14 N2-1574+05
N1-1576+65
N1-1576+67
N1-1583+02
N1-1584+69
N1-1584+87
N1-1589+54
N1-1604+92 N2-1605+08
N1-1614+97
N1-1620+97 N2-1620+97
N1-1621+40 N2-1621+56
N1-1668+73
N1-1674+27
N1-1675+00
N1-1677+98
N100 EMR
N100 EMR and EMR S100
N101 ECR
N101 ECR
N102 Elect Cab Rm
N102 Fire Command Center
N102 Yard Storage Rm
N103 Elect Cab Rm
N103 Electrical cabinet Room
N104 ECR
N104 ECR
N105 ECR
N105 EMR
N106 Elect Cabinet Rm
N106 Yard Storage Rm
N107 Yard Storage Rm
N12 interlocking Switch 5B
N2 1185+29
N2 1195+76
N2-1047+62
N2-1140+70
N2-1143+48
N2-1159+10
N2-1162+09
N2-1163+95
N2-1163+96
N2-1166+09
N2-1169+09
N2-1181+58 and N1-1198+28
N2-1213+10
N2-1216+96
N2-1217+93
N2-1240+57
N2-1294
N2-1509+00
N2-1532+71
N2-1555+68
N2-1573+04 OB
N2-1612+38 N2-1613+94
N2-1655+76
N2-1659+55
N2-1659+61
N2-1660+85
N2-1666+43
N2-1667+91
N2-1668+71
N2-1677+00
N2-1677+98
N2-1678+00
N4 cm 1193+00
N96 and N09
N96 Interlocking
N98A crossover (Yard Junction)
N98A TCR
N98B YL2-2+92
Next to the west safe dispersal area, both sides
Norh Pavilion Elevator Machine room
North and South Pavilions
North and South Ped Bridges
North Pavilion
North Pavilion Elevators
North Pavilion entrance
North pavilion Escalator 01
North pavilion Escalators
North Pavilion Ped Br Lighting
North Pavilion sidewalk
North Pavilion Site
North Pavilion street level
North Pavilion walls and pits
North Pavilion, escalator 2 side
North Pavilion, street level
North Ped Bdge, Support S-4
North Ped Bridge
North Ped Bridge Support S3
North Ped Bridge entrance
North Ped Bridge Support S3
OB side CL-24 & 25
OB trackwall at cm 1193+00
OB trackwall at cm 1195+23
Open Platform
Pavilion
Pavilion elevators lobby, mezz level
Pavilion façade
Pavilion, between Elevator Machine Room and elevators
Pavilions
Ped Bridges, At several supports, north and south sides
Pedestrian Bridge
Pedestrian Bridges
Pier 27 North
pier 3
Platf Level
Platform
Platform ACC-103, located under mezzanine deck, over platform
Platform ceiling
Platform ceiling, CL13.5, IB side
Platform ceiling, CL13.5, IB side.
Platform ceiling, CL13.9, IB side
Platform ceiling, CL14.5, IB side
Platform ceiling, CL14.7, IB side.
Platform ceiling, CL2.9, OB side.
Platform ceiling, CL3.4, Axis E (center platform).
Platform ceiling, CL5.5, IB side.
Platform ceiling, CL6.5, IB Side, over the train way.
Platform ceiling, CL6.5, IB Side, platform edge.
Platform ceiling, CL6.9, IB Side, over the train way.
Platform ceiling, CL7.2, IB Side, over the train way.
Platform ceiling, CL7.5, IB Side, over the train way.
Platform Cl 13.5 IB side
Platform Cl 15.5 IB side
Platform Cl 17.9 OB side
Platform Cl 18.8 IB side
Platform CL 2.8 OB side
Platform Cl 20.2 OB side
Platform CL 3.5 IB side
Platform CL 6.6 IB side
Platform CL 7.1 IB side
Platform CL 7.5 IB side
Platform CL 7.6, IB side, next to EMR
Platform CL-10 IB side
Platform east and west end gates
Platform East and West Safe Dispersal Areas
Platform East precast wall and windscreens throughout the platform
Platform East Safe Dispersal Area IB side
Platform expansion joints
Platform Handrails to East Safe Dispersal Area
Platform level
Platform Level CL 14 - 15
Platform level CL-1
Platform level, East end
Platform Level, OB next to stair 4
Platform level, west end
Platform level, West end sevice aisles
Platform level, west end wall
Platform PA speakers
Platform Service Aisles to West Safe Dispersal Area, Both sides
Platform shelters
Platform- closed
Platform, IB CL2.4
Platform, around mid point
Platform, CL 15 & 16
Platform, CL 4.5, IB next to EMR
Platform, east and IB side
Platform, East and West Safe Dispersal Areas
Platform, East End OB side
Platform, East Safe Dispersal Area
Platform, east side
Platform, East side, IB
Platform, IB CL 3.4
Platform, IB Side
Platform, IB Side (N1)
Platform, IB Side- closed
Platform, Sidewalks west of CL-05 IB Side
Platform, towards the east side
platform: Escalator 6
Platform: Escalators 5 & 6
Plenum area
Plenum area, CL 01, IB side
Plenum area, CL 12.3, IB side
Plenum area, water service room and washrooms.
Plenum area; Between CL 01 and 1, IB side
Plenum area; CL 10.9 IB side
Plenum area; CL 13.3 IB side
Plenum area; CL 15.7 IB side
Plenum area; CL 18.7 IB side
Plenum area; CL 19 OB side
Plenum area; CL 20 IB side
Plenum area; CL 4.5, IB side
Plenum area; CL 4.8, IB side
Plenum area; CL 8.9, IB side
Plenum below Elevator Machine Room
Plenum below elevator machine room
Plenum below Elevator Machine Room to elevators 5&6
Plenum, Below Elevator Machine Room
Plenum, Below Elevator Machine Room4
Plenum; CL 21.5 IB Side
Plenum; CL 21.5 OB Side
Project wide, where the signs are mounted to the chain link fence
Projectwide
PT-06 Airport Fan Room
Public washrooms exterior wall
PublicWashrooms roof
Reston and Herndon Stations track level, both sides
RL 1-N, Emergency Egress Stairs 114, Platform Level
RL 1-S, Platform Ceiling, CL1.9 Axis F
Roof level over AC Switchgear Room, CL-1 IB Side
S. Pav Esc 3
S100 EMR
S101
S101 EMR
S102 Elect Cabinet Rm
S102 South Pavilion, next to S102 Elect Cab Rm
S103 Elect Cab Rm
S103 Fire Command Center
S103 Fire Command Center
S104 ECR
S105 ECR
S106 Yard Storage Rm
S107
S107 Elect Cab Rm
S107 South Pavilion Electrical Cabinet Room - S107
S107 Yard Storage Rm
Safety walks
See NCR-0136 for specific 84 and 72" girders. All 96" girders with this deficiency were scrapped
Service Aisle to East Refuge Area
Service Aisles to East Safe Dispersal Area
Signal 8 at N2-1531+79
Signal bases in ballasted areas
Single Cross Over & Turn Out
Site, North Pavilion
Snow Melters
South and Nort Pedestrian Bridges and Pavillion Entrances
South and North Pavilion
South and North Pedestrian Bridges and Pavillion Entrances
South Pavilion
South Pavilion East & North walls
South Pavilion Elevator Lobby
South Pavilion Elevators street level
South Pavilion Elevators
South Pavilion Escalator 1
South Pavilion escalators
South pavilion foundation slab
South Pavilion next to Ped Brdg
South Pavilion sidewalks
South Pavilion street level
South Ped Bridge
South Ped Bridge Support S7
South Ped Bridge Support S8
South Ped Bridge Support S8, West side
South Ped Bridge Support S9, East Side
Spans 75 to 79
splices- closed
Sta. 1280+00 approx.
Sta. 1339-1345 approx., IB
Staion and NP.MH.01
Stair #3
Stair 4
Stairs 3 & 4 middle landing
Stairs 5
Station
Station AC Swchbd Rms, CERs, Telecomm Rms, Esc. Cntrl Rms, Kiosks, Pavilion Elec Cabinet Rms,
Station AC Swchbd Rms, Pavilion Elec. Cabinet Rms, Telecomm Rms, Esc. Cntrl Rms,
Station barrier wall
Station elevators
Station Ground Grid - West Side of Station
Station Platform
Station platforms
Steel- closed
Switch machine 5B
Switch Machines
Systemwide DXO
TBS 06 Comm. Rm.
TBS 10
TBS 11 - North Wayside Structure (near DS #14
TBS 6
TBS 6 ATC Bldg
TBS 6 Comm Bldg
TBS 6, 7, 8, 9, 10, 11
TBS 7 ATC/COMM Rm
TBS 9
TCR
TCR Doors
Third Rail Heat Tape Installation
Throughout the platform
Throughout the Station
TPSS 12
TPSS 12 Comm bldg
TPSS 12 north side
TPSS 12 Transformer yard
TPSS 13
TPSS 13 Comm Bldg
TPSS 13 Transformer Yard
TPSS 14
TPSS 14 Comm Bldg
TPSS 14 Containment Pit
TPSS 14 Ground Grid
TPSS 14 Transformer yard
TPSS 14 Vista Switches Couryard
TPSS 14 Wayside 34.5MH.01
TPSS 14, Manhole PMH.03
TPSS 15
TPSS 15 ATC Bldg
TPSS 15 COMM & TCR Room
TPSS 15 Comm Bldg
TPSS 15 Transformer yard
TPSS 15 Vista Switches
TPSS 15, Transformer side
TPSS 17
TPSS 17 COMM Room
TPSS 18
TPSS 18 LVMH.01 and PMH.03
TPSS 18 MH-01
TPSS 18.CMMH.01
TPSS 19
TPSS 19 Wayside 34.5MH.01
TPSS 19, vista switch side
TPSS 20
TPSS 20 Wayside near COL. - A11
Track area, both sides, subgrade level
Track bed, both sides
Track level, OB Side
track wall
Track wall fence between N06 and N07
Track Walls between Centreville Bridge and Innovation Station
Track, Along trackwall East Refuge Area, OB side
Track, CM 1290+31
Track, N1-1266+23
Track, N1-1271+99
Track, N1-1290+69
Track, N1-1291+10
Track, N1-1312+63
Track, N1-1312+65
Track, N1-1358+40
Track, N1-1359+13
Track, N1-1372+47
Track, N1-1393+31 to 1405+08
Track, N2-1266+90
Track, N2-1271+99
Track, N2-1297+40
Track, N2-1297+51
Track, N2-1312+64
Track, N2-1326+15
Track, N2-1338+00
Track, N2-1358+39
Track, N2-1359+13
Track, West of Passenger Station, OB, Highway Side.
Trackside
Trackway
Trackway , between Horsepen Bridge and Abutment A
Trackway OB side
Trackway, at mid platform, both sides
Trackway, west end
Typical for all Hair dryers termination in conflict with the 3rd rail guards
Under Platform CL21.7, Center corridor
Under Platform CL22.1, IB side
Under the platform, CL 19.8, OB side
Under the platform; CL21.6
Under the platform; CL7.9, IB side
Various-Tracks
Wayside where the boundary of the two locations meet.
West of Reston Station, sta. 1141+80 approx. IB side
West of Reston Station, sta. 1141+80 approx. OB Side
West Safe Dispersal Area
West Service Aisle
YL-3 CM-1+41
YL3-1+41